SAMPLE SPECIFICATION

Note:  Modify the items in italics according to your specific job requirements.

ITEM L-125 INSTALLATION OF L-861T(L) LED LIGHTS WITH AND WITHOUT HEATER

DESCRIPTION

125-1.1 This item shall consist of furnishing and installing the L-861T(L) LED fixtures in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures. It shall also include the testing of the installation and all incidentals necessary to place the lights in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

125-2.1 L-861T(L).  The L-861T(L) LED fixtures shall conform to the requirements of FAA Advisory Circular 150/5345-46 (current edition) “Specification for Runway and Taxiway Light Fixtures” and “FAA Engineering Brief No. 67 “Light Sources other than Incandescent and Xenon for Airport Lighting and Obstruction Lighting Fixtures.” The L-861T(L) LED fixture shall be ETL certified.   The L-861T(L) LED fixtures shall be a fixture as manufactured by AIRPORT LIGHTING COMPANY (www.airportlightingcompany.com) or approved equal.

125-2.2 EQUIPMENT SUPPLIED.  L-861T(L) LED fixtures shall be supplied for the total quantity as shown on the plans.  Each lot shipment of fixtures shall include one Instruction Manual.  It shall be possible to download additional manuals from the manufacturer’s web site.

125-2.3 L-861T(L) LED FIXTURE.  The light source shall be an electroluminescent diode assembly.  To ensure reliability, a single LED shall be used in the light source.  The lifetime of the LED shall be a minimum of 100,000 hours at full intensity and more than 180,000 hours in actual operating conditions.  
{To ensure optimum daytime visibility & survivability during knockover events, the optical emitting lens shall use an aviation blue borosilicate glass.}

The light fixture, with heater, shall operate on a 6.6A or 20A circuit at 60Hz {50Hz} using an appropriately-sized isolation transformer with a 6.6A secondary.  For increased efficiency, the fixture without heater shall operate with a 10/15W, 6.6A (secondary) isolation transformer that meets all applicable requirements of AC 150/5345-47.  The fixture load with the heater operational shall be no more than 25VA. The CCR load (which includes isolation transformer losses), with the heater operational, shall be no more than 30VA. The fixture load with the heater inactive shall be no more than 12VA.  The CCR load, with the heater inactive, shall be no more than 18VA.  The heater shall be designed to ensure that the light emitting area remains unobscured and clearly visible in a manner similar to existing incandescent fixtures.  Activation of the heater shall be thermostatically controlled.

The fixture shall have an adjustment mechanism that allows ±4° vertical adjustment in the field.  It shall be possible to install the lights on existing circuits in addition to, or in replacement of, conventional incandescent or halogen lights without having to change any other element (CCR, primary and secondary cabling, series isolation transformer, etc.).  The fixture light output shall match quartz-incandescent fixtures at all brightness levels.

It shall be possible to easily remove the top optical assembly without the use of tools.  Exterior, hard to remove, rubber type elements (that are subject to UV degradation; attack by rodents, fire ants, birds, etc) shall not be used to hold the top optical assembly on.

The fixture electronics shall be mounted inside the LED chamber to provide optimum protection from water and ice in the base can.  No active electronic LED elements are allowed in the base can.  The fixture shall use robust, solid-state internal devices that withstand damage if the fixture is knocked over.  To insure long-reliability, the heater shall be mounted in the fixture head assembly.  Heater wires taped to the inside optical element, that are subject to long-term degradation, shall not be used. It shall be possible to remove the top optical assembly without unplugging any heater wiring.

The overall fixture height shall be 14 inches {20 inches} {24 inches} {30 inches}.

CONSTRUCTION METHODS

125-3.1 PLACING THE L-861T(L) LED FIXTURES.  The contractor shall furnish and install each L-861T(L) LED fixture as specified in the proposal and shown in the plans.  The L-861T(L) LED fixtures shall be mounted on an industry standard 1.5-inch {2-inch} slip fit hubbed frangible coupling.  The fixture shall then be mated to a standard FAA L-867 base at the locations shown on the plans.

125-3.2 TESTS.  All taxiway edge lights shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance.  The test shall include operating the constant current regulator in each step not less than 10 times at the beginning and end of the 24-hour test.  The fixtures shall illuminate properly during each portion of the test.

METHOD OF MEASUREMENT

125-4.1 MEASUREMENT.  The quantity of lights to be paid for under this item shall be for the total quantity of L-861T(L) LED fixtures installed and one Instruction Manual (per lot) and accepted as completed units, in place, ready for operation.

BASIS FOR PAYMENT

125-5.1 PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of L-861T(L) LED fixtures installed, in place by the Contractor, and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-125-5.1 	L-861T(L) LED fixtures, in Place—per each

END OF ITEM L-125