SAMPLE SPECIFICATION

Note:  Modify the items in italics according to your specific job requirements.

ITEM L-125 INSTALLATION OF HIGH INTENSITY L-862(L) and L-862E(L) LED LIGHTS

DESCRIPTION

125-1.1 This item shall consist of furnishing and installing the High Intensity L-862(L) and L-862E(L) LED fixtures in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures. It shall also include the testing of the installation and all incidentals necessary to place the lights in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

125-2.1 The L-862(L) and L-862E(L) LED fixtures shall conform to the requirements of the current edition of FAA Advisory Circular 150/5345-46 “Specification for Runway and Taxiway Light Fixtures” and “FAA Engineering Brief No. 67 “Light Sources other than Incandescent and Xenon for Airport Lighting and Obstruction Lighting Fixtures.”  The L-862(L) and L-862E(L) LED fixtures shall be ETL certified.  {The fixture shall also conform to ICAO Annex 14, Volume 1, paragraph 5.3.9.10 for Precision Approach Runway and Transport Canada specification TP 312.}  The L-862(L) and L-862E(L) LED fixtures shall be manufactured by AIRPORT LIGHTING COMPANY (www.airportlightingcompany.com) or approved equal.

125-2.2 EQUIPMENT SUPPLIED.  FAA L-862(L) and L-862E(L) LED fixtures shall be supplied for the total quantity as shown on the plans.  Each lot shipment of fixtures shall include one Instruction Manual.  It shall be possible to download additional manuals from the manufacturer’s web site.

125-2.3 L-862(L) AND L-862E(L) LED FIXTURE.  The light source shall be an electroluminescent diode (LED) assembly.  The lifetime of the LED shall be a minimum of 56,000 hours at full intensity and more than 100,000 hours in actual operating conditions.  The fixture light output shall match quartz-incandescent fixtures at all brightness levels on a 3-step or 5-step regulator as defined in FAA Engineering Brief 67.

To ensure daytime recognition of L-862E fixtures will have a lens retainer with a visible surface area of greater than 2 ½ square inches and colored to match the light output.  The L-862 fixtures will have a yellow lens retainer.  (EB67, para 2.8).  To ensure long-life, clarity and survivability, the lens will be made from glass meeting MIL-C-7989B specification.  To minimize power consumption all lenses will be clear.

It shall be possible to install the lights on existing circuits in addition to, or in replacement of, conventional incandescent or halogen lights without having to change any other circuit element (CCR or primary and secondary cabling).  The light fixture must be designed to operate when connected to any ferroresonant or thyristor (SCR) type CCR that complies with IEC or FAA specification requirements.

The fixture can be supplied with an optional arctic kit.  The light fixture shall be designed to operate on either a 4.8A to 6.6A 3-step or a 2.8A to 6.6A 5-step airfield series circuit at 60Hz {50Hz} using an appropriately sized isolation transformer.  The fixture load shall be no more than 45VA and shall use a 30/45W isolation transformer.  Fixtures with optional arctic kits, the fixture load shall be no more than 59VA and shall use a 65W isolation transformer.

Each fixture must be set with the proper toeing (4.5° for L-862 and L-862E Green) at the factory.  The fixture shall have a leveling mechanism that allows ±4° vertical adjustment in the field.  The cordset entry into the fixture shall be secured with a strain relief.  The fixture is designed to evacuate all moisture.  The sealed lens assembly has a vent to evacuate all condensation.

In order to provide optimum protection from water and ice in the base can, the fixture electronics shall be mounted above ground in the fixture top optical assembly.  No active electronic LED elements are allowed in the base can.  The fixture shall use robust, solid-state internal electrical devices that withstand damage if the fixture is knocked over.   The overall fixture height shall be 14 inches {24 inches} {30 inches}.

The fixture shall have a cap to eliminate the need for an aiming device.  The cap has grooves for a torpedo level to allow for easy aiming and leveling

CONSTRUCTION METHODS

125-3.1 PLACING THE L-862(L) AND L-862E(L) LED FIXTURES.  The contractor shall furnish and install each L-862(L) and L-862E(L) LED fixture as specified in the proposal and shown in the plans.  The L-862(L) LED and L-862E(L) fixtures shall be mounted on an industry standard 1.5-inch {2-inch} slip fit hubbed frangible coupling.  The fixture shall then be mated to a standard FAA L-867 base can at the locations shown on the plans.  Each fixture must then be leveled and aimed in azimuth.

125-3.2 TESTS.  All L-862(L) runway edge and L-862E(L) runway end lights shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance.  The test shall include operating the constant current regulator in each step not less than 10 times at the beginning and end of the 24-hour test.  The fixtures shall illuminate properly during each portion of the test.

METHOD OF MEASUREMENT

125-4.1 MEASUREMENT.  The quantity of lights to be paid for under this item shall be for the total quantity of L-862(L) and L-862(L)E LED fixtures installed; one aiming device; and one Instruction Manual (per lot) accepted as completed units, in place, ready for operation.

BASIS FOR PAYMENT

125-5.1 PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of L-862(L) and L-862E(L) LED fixtures installed, in place by the Contractor, and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-125-5.1 	L-862(L) and L-862E(L) LED fixtures, in Place—per each

END OF ITEM L-125