# LED L-859(L) STYLE F ODAL – SAMPLE SPECIFICATION

Note: Modify the items in italics according to your specific job requirements.

ITEM L-125 INSTALLATION OF LED L-859(L) Style F ODAL

# DESCRIPTION

125-1.1 This item shall consist of furnishing and installing the omni-directional LED L- 859(L) Omni Directional Approach Lights in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures. It shall also include the testing of the installation and all incidentals necessary to place the lights in operation as completed units to the satisfaction of the Engineer.

# EQUIPMENT AND MATERIALS

125-2.1 L-859(L) STYLE F. The LED L-849 Style F ODAL shall conform to the requirements of FAA Advisory Circular 150/5345-51 “Specification for Discharge-Type Flashing Light Equipment” and FAA LED “Engineering Brief No. 67” (current editions). The LED L-859(L) ODAL shall be certified to current FAA Advisory Circulars. The LED L-859(L) ODAL shall be as manufactured by AIRPORT LIGHTING COMPANY (www.airportlightingcompany.com) or approved equal.

125-2.2 EQUIPMENT SUPPLIED. The LED L-859(L) ODAL system shall be supplied for the total quantity as shown on the plans. Each LED L-859(L) ODAL system shall include one Instruction Manual. The manufacturer shall also have a downloadable electronic version of the manual available on their web site.

The LED ODAL system shall consist of the following classifications:

- Type.

{L-859(L)V – ODAL powered by airport voltage power source.

## or

L-859(L)I – ODAL powered by an airfield series circuit.}

- Style.

Style F - Omnidirectional, three brightness steps.

The LED ODAL system must operate at temperatures from –40 to +131°F (–40 to +55°C).

125-2.3 ODAL SYSTEM. The LED L-859(L) Style F ODAL shall provide a flashing visual indication to pilots of the runway centerline and  threshold during an approach. To ensure reduced energy consumption, reduced maintenance requirements and elimination of costly xenon lamp replacement, the L-859(L) fixture light source shall be a Light Emitting Diode (LED) assembly. Xenon flashtubes or HID lamps will not be accepted. The Primary and Secondary ODAL units shall be placed at the runway threshold and five additional units will be placed in line with runway centerline. All units will have a flash rate of 60 flashes per minute ±10%. Both the Primary and Secondary REIL units shall flash simultaneously with no more than a 10-millisecond difference between them. The five centerline lights will flash sequentially starting with furthest light from the threshold.

{125-2.4 VOLTAGE POWERED REIL. The voltage powered ODAL shall operate from a power supply of 95-264VAC (3-wire with the center wire being neutral), 50/60Hz.

[The L-859(L) Style F shall have a maximum total CCR load of 194VA per unit.]

## or

{125-2.4 CURRENT POWERED REIL. The series circuit powered LED ODAL system shall operate from either a 3 or 5-step, 60Hz [50Hz] series lighting circuit.

[Each L-859(L) Style F cabinet shall be separately powered with a 6.6A secondary, 100W maximum isolation transformer.]

125-2.5 ODAL OPERATION. {To maximize maintenance personnel safety, there shall be no more than 240Vdc at any point inside either L-859(L)I control cabinet.} or {To maximize maintenance personnel safety, there shall be no more than 70Vdc at any point inside either L-859(L)V control cabinet.} Each control cabinet shall include a door interlock switch that deactivates incoming power when the door is opened. DPDT dry relay output contact points shall be present to provide an external indication in case of a system fault. A system fault alarm shall be activated if 1.) There is a loss of input power,

2.) If more than 25% of the LEDs fail.

A flasher control board in the control cabinet shall generate a trigger signal, which shall be transmitted to the LED flasher assemblies in both Primary and Secondary control cabinets. The trigger signal shall be sufficiently robust such that the Primary to Secondary cable does not need to be shielded.

{The LED L-859(L) ODAL shall be available with either one- or three-step current sensing to allow automatic intensity selection based on the current sensed in a series circuit.}

{The L-859(L)V ODAL Primary control cabinet shall have the capability to read series circuit current from the secondary of a 6.6A isolation transformer } or {The L-859(L)I ODAL Primary control cabinet shall have the capability to read series circuit current from the secondary of the same isolation transformer that powers the Primary. Use of a separate isolation transformer shall not be required.}

# CONSTRUCTION METHODS

125-3.1 PLACING THE LED L-859(L) ODAL. The contractor shall furnish and install each L-859(L) ODAL as specified in the proposal and shown in the plans. The L-859(L) ODAL shall be mounted on a mounting device at the locations shown on the plans.

{If current sensing used: The current sensing PCB shall be properly adjusted to activate the ODAL at the appropriate CCR step settings}

125-3.2 TESTS. The ODAL shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance.

{If current sensing used:

With the ODAL in Remote, the test shall include operating the constant current regulator in each step not less than 10 times at the beginning and end of the 24-hour test. The ODAL shall illuminate properly during each portion of the test. At the end of this test, the ODAL shall be checked for proper operation in Local control}

{If current sensing not used:

The test shall include operating the ODAL in both Remote and Local in each step not less than 10 times at the beginning and end of the 24-hour test. The ODAL shall illuminate properly during each portion of the test.}

# METHOD OF MEASUREMENT

125-4.1 MEASUREMENT. The quantity of lights to be paid for under this item shall be for the total quantity of LED L-859(L) ODAL units installed and one Instruction Manual (per system) and accepted as completed units, in place, ready for operation.

# BASIS FOR PAYMENT

125-5.1 PAYMENT. Payment will be made at the contract unit price for the completed total quantity of LED L-859(L) ODAL units installed, in place by the Contractor, and accepted by the Engineer. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-125-5.1 LED L-859(L) ODAL units, in Place—per each

END OF ITEM L-125